Ultrasonic level gauge user's Guide

JXBS-3001-CSB-YWJ

Ver1.0

# Chapter 1 Product Introduction

## 1.1 Product overview

Ultrasonic level gauge is a distance measuring instrument developed based on the principle of ultrasound. It uses the transmitted sound wave pulse to measure the time at the receiving end to calculate the distance. The shell of the whole machine is made of ABS material, which has the characteristics of light weight, no moving parts, sturdiness and durability, and does not require maintenance and on-site calibration. It can be used in conjunction with computers, data collectors or other RS485-compliant collection equipment. It is widely used in the liquid level distance measurement of industrial water tanks, tanks, municipal engineering, water conservancy and hydropower, sewage treatment, petrochemical industries and other industries.

## 1.2  main parameters

| parameter | Technical index |
| --- | --- |
| Range selection | 5m、10m、20m、30m |
| measurement accuracy | 0.5%FS-1%FS |
| Resolution | 0.001m |
| Measurement dead zone | 0.4m~1m（Varies according to the range） |
| way of communication | RS485/GPRS/4G/4-20mA |
| Baud rate | 19200/9600/4800/2400 |
| Power supply | 12VDC |
| Working current | Turn on the backlight：130±10mA Turn off the backlight：70±10mA |
| Operating temperature | -20~+60℃ |
| Working humidity environment | 0~100%RH（15~95%RH） |

## 1.3 Features

◆ No moving parts, low wear and long service life;

◆ Engineering plastic shell, lightweight design, portable, easy to install and disassemble

◆ Convenient signal access, support 485-RTU;

◆ No maintenance and on-site calibration are required.

# Chapter 2 Hardware Connection

## 2.1 Inspection before equipment installation

Please check the equipment list before installing the equipment:

| name | Quantity |
| --- | --- |
| High precision sensor | 1set |
| 2G module sensor | 1set（Optional） |
| 12V waterproof power supply | 1set（Optional） |
| USB to 485 device | 1set（Optional） |
| Warranty card/certificate | 1 serving |

### Appearance Gallery:

### 2.1.1Wiring

|  | Thread color | Description |
| --- | --- | --- |
| power supply | brown | Power 12V positive |
|  | black | Power supply 12V negative |
| Communication | yellow | 485A |
|  | blue | 485B |

The factory default provides 0.6 meters long wire, customers can extend the wire as needed or wire in order.

## 3.1 Analog quantity wiring method

The power interface is a wide voltage power input of 12V. For analog products, pay attention to the positive and negative signal wires, and do not reverse the positive and negative current/voltage signal wires.

|  | Thread color | Description |
| --- | --- | --- |
| power supply | brown | Positive power supply (12V DC) |
|  | black | Power negative |
| Communication | blue | Current output positive (m) |

Precautions:

(1) Please be careful not to connect the wrong wiring sequence, the wrong wiring will cause the equipment to burn

(2) The voltage/current positive output is an active output. Never connect the voltage/current positive output to the positive position of the power supply, which will definitely cause burnout.

(3) The factory default provides 0.6 meters long wire, customers can extend the wire as needed or wire in order.

## 4.1 Equipment installation

First, unscrew the rotating nut and a layer of rubber ring at the bottom of the device, then fix the device to the probe fixing plate, and finally install the rubber ring and rotating nut.

The position of the fixing hole of the 5m range probe bracket is as follows

The emitting surface of the probe should be lower than the bottom of the receiver, and the axis of the sensor should be as perpendicular to the measured surface as possible. In the case of smooth side walls, the distance between the probe and the side wall should not be less than the range *tan10, for example, the distance between the probe and the side wall should not be less than 0.9 meters in the 5 meter range; when the side wall is rough and uneven, a large amount of False echo, at this time, the distance between the probe and the side wall should not be less than the range *tan20, for example, the distance between the probe and the side wall should not be less than 1.8 meters.

Avoid any other objects in the launch angle of the probe, such as pipes, brackets, etc.

Ultrasound will be attenuated in the presence of dust, mist, and ripples on the liquid surface, and a large-range ultrasonic probe needs to be used appropriately.

The measuring position of the probe should avoid sharp fluctuations directly below.

# Chapter 2 Communication Protocol

## 2.1 Basic communication parameters

| parameter | content |
| --- | --- |
| coding | 8-bit binary |
| Data bit | 8-bit |
| Parity bit | no |
| Stop bit | 1-bit |
| Wrong calibration | CRC lengthy cyclic code |
| Baud rate | 2400bps/4800bps/9600 bps can be set, the factory default is 9600bps |
| coding | 8-bit binary |

## 2.2 Data frame format definition

Adopt Modbus-RTU communication protocol, the format is as follows:

Initial structure >= 4 byte time

Address code = 1 byte

Function code = 1 byte

Data area = N bytes

Error check = 16-bit CRC code

End structure >= 4 bytes time

Address code: the address of the transmitter, which is unique in the communication network (factory default 0x01).

Function code: The command function prompt sent by the host, this transmitter only uses function code 0x03 (read memory data).

Data area: The data area is the specific query data area, pay attention to the 16bits data high byte first

CRC code: two-byte check code.

Interrogation frame

| address code | function code | Register start址 | Register length | Check code low bit | Check code high |
| --- | --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 2 byte | 2 byte | 1 byte | 1 byte |

Reply frame

| address code | function code | Effective bytes | Data area | Second data area | Nth data area |
| --- | --- | --- | --- | --- | --- |
| 1 byte | 1 byte | 1 byte | 2 byte | 2 byte | 2 byte |

## 2.3 Register address

| Register address | PLC configuration address | content | operating |
| --- | --- | --- | --- |
| 0003H | 40004 | Measurement value (level value or liquid level value) | Read only |
| 0100H | 40101 | Device address (0-252) | Read and write |
| 0101H | 40102 | Baud rate(2400/4800/9600) | Read and write |

## 2.3 Communication protocol example and explanation

### 2.3.1 Read the measured value of the device address 0x01

Interrogation frame

| address code | function code | initial address | Data length | Check code low bit | Check code high |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x00,0x03 | 0x00,0x01 | 0x74 | 0x0A |

Reply frame(For example, the measured value is 1.234m)

| address code | function code | Effective bytes | Distance value | Check code low bit | Check code high |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x03 | 0x02 | 0x04 0xD2 | 0x3A | 0xD9 |

04D2 H (hexadecimal)=1234=>distance=1.234m

### 2.3.2 Modify the device address of device address 0x01

Inquiry frame (for example, modify the device address to 0x02)

| address code | function code | initial address | change the data | Check code low bit | Check code high |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x06 | 0x01,0x00 | 0x00,0x02 | 0x09 | 0xF7 |

Reply frame

| address code | function code | initial address | change the data | Check code low bit | Check code high |
| --- | --- | --- | --- | --- | --- |
| 0x01 | 0x06 | 0x01,0x00 | 0x00,0x02 | 0x09 | 0xF7 |

# Chapter 3  Function Description

3.1 Product button usage description

| button | Menu screen | Content screen |
| --- | --- | --- |
| Long press the SET button | return the main screen | return the main screen |
| Short press the SET button | Enter options | confirm |
| Long press the UP button | Return to the previous menu | Value +100 |
| Short press the UP button | On the turn | Value +1 |
| Long press the DOWN button | no | Value -100 |
| Short press the DOWN button | Flip down | Value -1 |

## 3.2 Main screen display

The upper part of the horizontal line is the total length from the probe to the bottom of the pool set by the customer. The default is no more than 3 times the range.

The lower part of the horizontal line: 1 symbol 2 measurement value.

When the upper part of the symbol is black, it indicates the current measured distance value.

When the symbol is black at the bottom, it means the current measured level value.

## 3.3 Mode selection

The modes are divided into expert mode and simple mode: in the expert mode, you can set other functions; in the simple mode, you can quickly complete the configuration of the product through 2-step settings and put it into use.

## 3.4 Password management

You can turn on the password function according to your needs. The initial password is 0000, and you can turn it on and modify it yourself. The backup password is Weihai area code 0631 and cannot be modified to avoid forgetting the password.

## 3.5Range management

This item has been in accordance with the range purchased by the user before leaving the factory. If the user restores the factory settings by himself, he must adjust it according to the purchased product parameters.

## 3.6 Measurement mode

Can switch between level mode and liquid level mode.

## 3.7 Communication settings

The device address and device baud rate can be modified.

## 3.7 Backlight setting

You can choose to switch the backlight. When the backlight is on, you can choose the backlight time.

## 3.8 Reset selection

You can choose to restore factory settings.

# Chapter 4 Analog Communication

The analog sensor wiring is simple, only need to connect the wire to the designated port of the device.

The following figure shows the wiring method of the current sensor. When measuring, first adjust the multimeter to the "DC mA" position, and then connect the sensor's power cord (brown wire and black wire) to the power supply; the sensor's yellow ( Gray) colored wire means that the signal is connected to the red test lead of the multimeter, and the other end of the black test lead of the multimeter is connected to the black wire of the sensor. At this time, the measurement is "wind speed"; The other end is connected to the black wire of the sensor, and the "wind direction" is measured at this time.

## 4.1 Analog value conversion

Wind speed:

| Current value | variable |
| --- | --- |
| 4mA | 0 |
| 20mA | 500 |

The formula is wind speed=(I-4)*0.3125

The unit of I is mA. 4mA represents 0 point and 20mA represents the maximum range linear conversion.

## 4.1 Notes

Please check whether the packaging is intact, and check whether the transmitter model and specifications are consistent with the product you purchased; if you have any questions, please contact our company as soon as possible.

Before use, please confirm: whether the output voltage of the power supply is correct; the positive and negative of the power supply and the positive and negative wiring of the product; and read the product manual or consult our company. Any error in the wiring will cause irreversible damage to the transmitter.

# Chapter 5  Jingxun Cloud

## 5.1 How to access Jingxun Cloud

There are two ways to access Jingxun cloud server:

For networked devices that support the Jingxun unblocked ecosystem.

(1) Use the account to log in to the cloud server on the PC side, and add the device ID to the account, then you can view the device upload data through the PC side server;

(2) In the WeChat applet, scan the QR code ID of the device and add the device to the account to view the uploaded data of the device.

If you use a third-party product that is not Jingxuntong. Data can be uploaded to our cloud server according to the report docking agreement of our cloud server. Please contact pre-sales or after-sales for the specific protocol used in the cloud report.

### 5.2 Use of Jingxun Cloud

First, you need to enter the domain name (www.sennor.net) to enter the login interface of Pingset, as shown in the figure below:

Fill in the account password in the corresponding position to enter the main interface of the cloud server; the main interface contains the specific function items of the server and instructions for use. as the picture shows:

Figure Jingxun Cloud Management Interface

The functions of Jingxun cloud server include: data center, equipment center, camera management, trigger management, monitoring large screen, system language selection and setting and other functions.

"Data Center -> Map Display" can view the location of the device and the name of the device in the form of a map. This method can observe the number of devices bound at one time, which is very intuitive and suitable for display to government agencies.

"Data Center -> List Display" can view the number of bound devices and the names of the devices, suitable for statistical use.

"Data Center -> Graphical Display" can view the data through the ID of the searched device.

"Data Center -> Historical Data" can enter the ID of the device, and you can view the data uploaded by the device at any time.

"Device Center -> Device Management" can search device ID to view device data; click "Add Device" in the upper left corner to add devices, as shown in the following figure:

Figure Jingxun Cloud Device Adding Interface

Follow the prompts on the interface to add devices.

(1) "Name" can fill in what you need;

(2) "Equipment number" is the ID of the device, for example: 16F3F88714BB, just fill in this set of values in the "Equipment Number" column;

(3) The "Initial Password" column can be filled in or omitted, depending on your own needs;

(4) "Equipment grouping" is to add equipment to the groups you have divided, and the specific grouping is based on your needs;

(5) "Device Address" click the blue coordinate arrow on the right to enter the map, and then drag a blue arrow inside the map to locate the coordinates. After the coordinates are determined, click "confirm", and finally click " Add" to complete the addition of the device.

GPRS signal quality description：

| Signal range | 0-5 | 5-10 | 10-15 | 15-31 |
| --- | --- | --- | --- | --- |
| Signal state | Unable to connect to the network, data transmission is interrupted | Data reporting is unstable and data transmission will be interrupted | Data can be reported normally, occasionally lost data | Data upload is stable, no packet loss |

## Precautions

Please check whether the packaging is intact, and check whether the transmitter model and specifications are consistent with the product you purchased; if you have any questions, please contact our company as soon as possible.

Before use, please confirm: whether the output voltage of the power supply is correct; the positive and negative of the power supply and the positive and negative wiring of the product; and read the product manual or consult our company. Any error in the wiring will cause irreversible damage to the transmitter.

5.3 Warranty and after-sales

The warranty clauses follow the sensor after-sales clauses of Weihai Jingxun Changtong Electronic Technology Co., Ltd., the sensor host circuit part is guaranteed for one year, the gas-sensitive probe is guaranteed for half a year, and the accessories (shell/plug/cable, etc.) are guaranteed for three months.